QUENCH CHARGERS

180 kW ADLB DC Fast Charger

Commissioning & Test Guide

Physical Checks  •  Hardware Configuration  •  Software Configuration

| Field | Reference |
| --- | --- |
| Source procedure | 72115-0000-13-60_PLTP |
| Build variant | Mahindra 180 kW ADLB1 |
| Power stage | 6 × 30 kW modules → 180 kW, up to 1000 Vdc, dual CCS2 |
| DLB mode | quintupleCombo |
| Companion file | ADLB_180kW_Test_Checklist.xlsx (machine-readable test set) |

# How to use this guide

This guide walks through commissioning and functional testing of the 180 kW ADLB charger in the order an engineer should follow on site: physical integrity first, then hardware device settings, then software configuration and functional/OCPP testing. Each step is a checkbox with its pass value stated inline, and the relevant on-screen view is shown beside it so the same value can be set or read back through the software tools.

### Software interfaces used

| Interface | Address / Access |
| --- | --- |
| LWI – SECC (Gun A) | http://10.20.27.100 (EcoG Local Web Interface) |
| LWI – SECC-LE (Gun B) | http://10.20.27.101 |
| Application Board (AB) | http://10.20.27.50:3001/swagger |
| Router admin | http://10.20.27.1 (login admin / admin) |
| IO Mapper (readback) | SECC LWI → IO Mapper → data (live JSON key/value) |

Safety first.  All Section A electrical safety tests (insulation / HV) require the charger de-energised and the listed PE connections removed before applying test voltage. Do not energise the system until Section A is complete and passed.

# A. Physical Checks

Performed with the charger de-energised. These are manual inspections and instrumented safety tests – not automatable – and gate everything that follows.

## A.1  Mechanical assembly

Reference build – front, side (with power module stack / cable management) and rear views.

❑  PHY-001  Fabrication free of dents; paint and finish correct per GA drawing.

❑  PHY-002  Standard and customer (Mahindra) stickers present per AWI.

❑  PHY-003  All internal components carry labelling stickers.

❑  PHY-004  Mechanical assembly complete per mechanical TC; all joints tightened.

## A.2  Power wiring

Power section – input busbar, MCCB, AC contactor and module feeds (PLTP Fig. 2).

❑  PHY-005  Input busbar, MCCB and AC contactor routed/connected per Fig. 2.

❑  PHY-006  Proper lugs and torque at SPD, ELR, MCB, AC & DC contactors, and module input/output.

❑  PHY-007  Each module output routed to its correct DC contactor and gun.

Expected: Module → contactor → gun mapping correct for all 6 modules.

❑  PHY-008  Earth distributed from busbar to all points; panel body bonded to earth busbar.

❑  PHY-009  Power hardware torqued with paint mark applied (AC and DC).

❑  PHY-010  All cables strain-relieved.

## A.3  Control & communication wiring

❑  PHY-011  All control wiring per schematic (SMPS, relays, contactor coils, IMD, display, meters, TBs).

❑  PHY-012  Controller connectors fully seated – no loose connections.

❑  PHY-013  CAN bus shielded; 120 Ω termination at SECCLE (start) and PM2 (end).

❑  PHY-014  RS485 (IMD, AC/DC meters, Gun CP) shielded; 120 Ω termination at both ends.

❑  PHY-015  RJ45 sequence/tightness correct: Router → SECC, → SECC-LE, → AB.

## A.4  Electrical safety tests

❑  PHY-016  Insulation (Megger) test at 500 V – AC input (R,Y,B,N) shorted, to earth.

Expected: Resistance ≥ 10 MΩ.  Repeat for DC output (+,−) of both guns to earth.

❑  PHY-017  HV test at 1440 V (IS 17017) – AC input shorted, to earth.

Expected: Leakage current ≤ 5 mA.

Note: Disconnect PE from Controller, Router, SMPS, IMD, SPD, Power Modules, GNDF and main earthing before applying test voltage.

# B. Hardware Configuration

Device-level settings made by hand (DIP switches, meter keypads, dial settings) and the power-up pre-checks. Meter settings can be confirmed afterwards through IO Mapper readback.

## B.1  Pre-checks (continuity, earthing, power-up)

❑  HW-001  All fuse ratings correct; short links removed from 8-channel relay base.

❑  HW-002  Continuity on terminal-block links (XL, XN, 24V1, 0V1, 24V2, 0V2), earthing, SMPS1/2 outputs, AC-meter V↔MCCB.

❑  HW-003  No short circuit between 24V1 and 24V2.

Verify: Open circuit (must be isolated).

❑  HW-004  Power up via MCCB; confirm supply rail voltages.

Expected: AB jack = 5 V;  HMI jack = 24 V;  SECC_J1 = 24 V;  CPPP_J8 = 24 V;  SECC-LE_J1 = 24 V;  DC meter = 24 V.

❑  HW-005  All boards/HMI power on; touch screen responsive.

## B.2  Power module addressing

Set each module address via its DIP switch (binary).

| Module | Address (binary) |
| --- | --- |
| Power Module 1 | 0 (default) |
| Power Module 2 | 1 |
| Power Module 3 | 2 |
| Power Module 4 | 3 |
| Power Module 5 | 4 |
| Power Module 6 | 5 |

❑  HW-006  Power module addresses set 0–5 across the six 30 kW modules.

## B.3  ELR (earth-leakage relay)

GIC ELR – leakage current (IΔn) and trip time (Δt) dials.

❑  HW-007  ELR leakage current and trip time set.

Expected: Leakage current = 0.1 In (A);  trip time = 1 Δt (S).

## B.4  IMD (insulation monitoring device)

IMD address DIP block – enable switches 4 to 8 (10-switch block), same on both IMDs.

❑  HW-008  Both IMDs set to the same address – DIP 4 to 8 enabled.

## B.5  AC energy meter (Selec)

❑  HW-009  Primary CT current rating set.

Expected: CT Primary = 200 A;  Network = 3P4W.

Note: Confirm afterwards via IO Mapper: voltages/current/PF actual = display.

Left: phase-sequence check (hold V) → 'OK – CLK'.   Right: current-connection check (hold I) → '23'.

❑  HW-010  Phase sequence check (hold 'V' 3 s).

Expected: Display reads 'OK – CLK'.

❑  HW-011  Current connection check (hold 'I' 3 s).

Expected: Display reads '23' (L2 & L3 reversed – required).

Note: If it reads '0', swap CT S1/S2 on L2 & L3, reboot the meter, re-check until it reads '23'.

## B.6  DC energy meter (Dfun)

❑  HW-012  DC meter Modbus address, parity and shunt rating set (keypad password 1101).

Expected: Modbus address = Add-002;  Parity = None;  Shunt SH1 = 500 A, SH2 = 500 A.

# C. Software Configuration & Testing

Network, firmware, controller/AB configuration, communication readback, charging and OCPP. Most of these steps are readable/assertable through the software interfaces, so they map directly to the automatable items in the companion checklist.

## C.1  Router (network)

Model RB44 / Silbo. First-time setup over its own SSID (AP_…, password 12345678) at 192.168.1.1, then move it to the charger LAN.

Router login – admin / admin.

❑  SW-001  Router Ethernet/LAN set to static IP and updated.

Expected: IP = 10.20.27.1;  reachable on new address with admin / admin.

Network → Ethernet → set IP 10.20.27.1, then Save and Update.

❑  SW-002  WIFI client SSID & passphrase entered; router reaches internet (WAN up).

WIFI Settings – enter Client SSID and passphrase, then Save and Update.

## C.2  Controller firmware & configuration (SECC / SECC-LE)

EcoG LWI → Update View – upload the .ecog-update file, run to 100 %, reboot, verify version.

❑  SW-003  SECC (10.20.27.100) and SECC-LE (10.20.27.101) updated to target release; firmware verified after reboot.

Advance → Configuration. Set the four values below on BOTH controllers, then 'Load to device'. (The screenshot shows the per-module defaults 30 / 250 – these must be changed for the 180 kW build.)

❑  SW-004  Controller configuration set on SECC and SECC-LE, then loaded to device.

Expected: num_of_modules = 6;  maxKW = 180;  maxA = 500;  dlbMode = quintupleCombo.

## C.3  Application Board (AB) firmware & OCPP config

AB firmware update via command line: ab-update-win.exe --image <file>.ecog-update.

❑  SW-005  AB updated ('installation successful' + reboot); firmware verified via GET /release.

Swagger → POST /ocpp-client/config – edit and execute the OCPP config keys.

❑  SW-006  AB OCPP config set for this unit and verified via GET /ocpp-client/config.

Expected: chargingPointVendor = QUENCH;  chargingPointModel = customer name;  chargePointSerialNumber = unit serial;  protocol = ocpp1.6;  RFIDEnabled = true;  OCPPEndpointToBackend = customer CMS URL;  NumberOfConnectors = 2;  powerSaveInIdleMode per requirement.

❑  SW-007  Confirm AB OCPP power/current limits intended for the 180 kW build.

Verify: PLTP example shows maxPowerLimitInkW = 80 and maxCurrentLimitInAmps = 200 (a 60 kW reference) while the controller is set to 180 kW / 500 A. Confirm the intended AB values – do not auto-correct if this is a deliberate CMS-side cap.

Note: Also confirm the two heartbeat keys (HeartbeatInterval = 300 vs HeartBeatInterval = 30) and dataTransfer VendorsId = [MSIL] against this build.

## C.4  Communication readback (IO Mapper)

SECC LWI → IO Mapper → data. Confirm every device is online and live values are sane.

❑  SW-008  All 6 power modules communicating over CAN.

❑  SW-009  Meters & IMD online.

Expected: modbus.selec.online = true;  modbus.dfun_dc.online = true;  modbus.gongyuan_IMD.online = true.

❑  SW-010  IMD insulation resistance during cable check / charging.

Expected: 60000  (≥ 10 MΩ).  65535 indicates ≤ 10 MΩ (fault).

AC-meter values in IO Mapper.  Left: idle (L1 +, L2/L3 −).  Right: charging (all + , PF ≈ 0.9).

❑  SW-011  AC-meter sign convention correct (confirms CT direction).

Expected: Idle: avg PF +, Active L1 +, L2 −, L3 −.  Charging: avg PF + (≈0.9), L1/L2/L3 all +, only active_import_total rising, export = 0.

## C.5  Charging test (both guns)

Left: LWI Charge Overview – pilot 'B connected, HiCom active'.  Right: HMI live session screen.

❑  SW-012  Gun A pilot state on EV connect.

Expected: 'B connected, HiCom active'.

❑  SW-013  Authorize and run a session on Gun A; verify behaviour.

Expected: SOC matches vehicle;  EV demand current = supply current;  cable-check + pre-charge complete;  clean stop/finishing.

❑  SW-014  Repeat the full session on Gun B (SECC-LE, 10.20.27.101).

## C.6  OCPP & CMS

Swagger – POST /ocpp-client/config with CMS WebSocket URL + charger ID, then start and restart.

❑  SW-015  Connect to CMS (config → start → restart all return 200); cloud sign on HMI.

HMI – both guns 'Available' with CMS connected (cloud icon).

❑  SW-016  Authorization works by OTP, RFID and Remote; idle error codes verified across CMS log, screen and HMI alarm log.

Swagger – offline local authorization list (OTP idTag + two RFID, status Accepted, updateType Full).

❑  SW-017  Offline OTP + 2 RFID loaded into local auth list; verified via GET.

### Energy reset after OCPP test

Dfun debug software – 'Meter Clear → Zero Clear' resets DC meter energy.

❑  SW-018  Reset AC meter energy (per AC-meter manual) and DC meter energy (Dfun 'Zero Clear').

End of guide. Record each item's result in the companion ADLB_180kW_Test_Checklist.xlsx (Actual / Result columns).