## README
180 kW ADLB DC Fast Charger - Commissioning / Test Checklist
Source document | 72115-0000-13-60_PLTP (Test Procedure for 180 kW ADLB Chargers)
Customer reference build | Mahindra 180kW ADLB1, DLB = quintupleCombo, 6 x 30kW modules
Column | Meaning
Test_ID | Stable ID for the test harness. Prefix = category (PHY / HW / SW).
Category | Physical ¦ Hardware Config ¦ Software Config
Section | Originating section of the PLTP document
Check_Item | What to verify
Expected_Value / Pass_Criteria | The value/state required to PASS. Use this as the assertion target.
Verification_Method | How the value is read (drives which automation interface applies)
Automatable | Yes = harness can read+assert via API/IOMapper/readback; Partial = needs a manual setup/EV but result is readable; No = physical/manual only
Source_Page | Page in the PLTP
Notes | Engineering notes, dependencies, and flagged discrepancies to verify (not auto-corrected)
Actual | Fill at runtime - value observed
Result | Fill at runtime - PASS / FAIL / N/A
Automation interface map
LWI SECC | http://10.20.27.100 (EcoG Local Web Interface)
LWI SECC-LE | http://10.20.27.101
AB Swagger | http://10.20.27.50:3001/swagger
Router admin | http://10.20.27.1 (admin/admin)
IO Mapper | SECC LWI > IO Mapper > data (JSON key/value readback)
Flagged discrepancy to confirm | AB OCPP example keys show maxPowerLimitInkW=80 / maxCurrentLimitInAmps=200 (a 60kW reference). For this 180kW build the SECC config sets maxkW=180 / maxA=500. Confirm the AB OCPP limits intended for 180kW before treating 80/200 as pass values - do NOT auto-correct if it is an intentional customer/CMS-side cap.

## Checklist
Test_ID | Category | Section | Check_Item | Expected_Value / Pass_Criteria | Verification_Method | Automatable | Source_Page | Notes | Actual | Result | Automation_Class
PHY-001 | Physical | 2.1 Mechanical | Fabrication free of dents; paint as per GA | No dents, correct paint/finish per Fig.1 GA | Visual | No | 5 |  |  |  | Manual
PHY-002 | Physical | 2.1 Mechanical | Standard + customer-specific stickers present | All stickers present per AWI & customer spec | Visual | No | 5 | Customer = Mahindra |  |  | Manual
PHY-003 | Physical | 2.1 Mechanical | Component labelling stickers inside panel | All internal components labelled | Visual | No | 5 |  |  |  | Manual
PHY-004 | Physical | 2.1 Mechanical | Mechanical assembly complete & connections tight | Matches mechanical TC; all joints tightened | Visual / torque | No | 5 |  |  |  | Manual
PHY-005 | Physical | 2.2 Power wiring | Input busbar, MCCB, AC contactor routing | Routing & connection per Fig.2 | Visual | No | 6 |  |  |  | Manual
PHY-006 | Physical | 2.2 Power wiring | Termination lugs at SPD/ELR/MCB/AC&DC contactors/PM I-O | Proper lugs, securely tightened | Visual / torque | No | 6 |  |  |  | Manual
PHY-007 | Physical | 2.2 Power wiring | Each module output routed to correct DC contactor & gun | Module-to-contactor-to-gun mapping correct | Visual | No | 6 | 6 modules |  |  | Manual
PHY-008 | Physical | 2.2 Power wiring | Earthing to busbar incl. panel body | Earth distributed to all points; body bonded to earth busbar | Visual / continuity | No | 6 |  |  |  | Manual
PHY-009 | Physical | 2.2 Power wiring | Power hardware torqued + paint mark (AC & DC) | Torque per spec; paint mark applied | Visual / torque | No | 6 |  |  |  | Manual
PHY-010 | Physical | 2.2 Power wiring | Cable stress relief | All cables strain-relieved | Visual | No | 6 |  |  |  | Manual
PHY-011 | Physical | 2.3 Control wiring | All control wires per schematic | Logic, controllers, fan, SMPS1/2 I-O, relays, coils, IMD, display, PSU, AC/DC TB, AC/DC meter wired per schematic | Visual vs schematic | No | 6 | Ref 72115-00-06-01_SCMT |  |  | Manual
PHY-012 | Physical | 2.3 Control wiring | Control cable routing, lugs, connectors | Per harnessing & AWI | Visual | No | 6 |  |  |  | Manual
PHY-013 | Physical | 2.3 Control wiring | Controller connectors seated | No loose connections | Visual / tug test | No | 6 |  |  |  | Manual
PHY-014 | Physical | 2.4 Comm wiring | CAN bus uses shielded wire + heat-shrink at strips | Shielded UNITRONIC CAN; controller->PM CAN | Visual | No | 6-7 |  |  |  | Manual
PHY-015 | Physical | 2.4 Comm wiring | 120 ohm CAN termination at SECCLE (start) & PM2 (end) | 120 ohm present both ends of CAN | Multimeter (bus off) | No | 7 |  |  |  | Manual
PHY-016 | Physical | 2.4 Comm wiring | RS485 2-core tinned-braid cable to IMD/AC mtr/DC mtr Ch1&2/Gun A&B CP | Correct shielded 2-core cabling | Visual | No | 7 |  |  |  | Manual
PHY-017 | Physical | 2.4 Comm wiring | 120 ohm RS485 termination at both ends | 120 ohm present both ends of RS485 | Multimeter (bus off) | No | 7 |  |  |  | Manual
PHY-018 | Physical | 2.4 Comm wiring | RJ45 tightness & sequence: Router->SECC, ->SECC-LE, ->AB | Correct pinout sequence; seated | Visual / cable tester | No | 7 |  |  |  | Manual
PHY-019 | Physical | 3.1 Insulation (Megger) | PE disconnected from listed components before test | PE off: Controller, Router, SMPS1/2, IMD, SPD, PM, GNDF, main earthing | Procedure step | No | 7 | Safety pre-step |  |  | Manual
PHY-020 | Physical | 3.1 Insulation (Megger) | AC input (R,Y,B,N) short to earth - insulation @500V | Resistance >= 10 Mohm | Insulation tester 500V | No | 7 | Input supply disconnected; AC busbar shorted |  |  | Manual
PHY-021 | Physical | 3.1 Insulation (Megger) | DC output (+,-) both guns short to earth - insulation @500V | Resistance >= 10 Mohm | Insulation tester 500V | No | 7 | DC outputs shorted |  |  | Manual
PHY-022 | Physical | 3.2 HV Test | PE & input supply disconnected from listed components | PE+supply off: Controller, Router, SMPS1/2/3, IMD, SPD, PM, GNDF, main earthing | Procedure step | No | 7-8 | Safety pre-step |  |  | Manual
PHY-023 | Physical | 3.2 HV Test | HV between shorted AC input & earth @1440V (IS 17017) | Leakage current <= 5 mA | HV tester 1.5kV | No | 8 | AC busbar R,Y,B,N shorted |  |  | Manual
HW-001 | Hardware Config | 4.1 Pre-check | All fuse ratings correct | Match BOM/schematic ratings | Visual | No | 8 |  |  |  | Manual
HW-002 | Hardware Config | 4.1 Pre-check | Short links removed from 8-channel relay base | All short links removed | Visual | No | 8 |  |  |  | Manual
HW-003 | Hardware Config | 4.1 Pre-check | Short links continuity: XL, XN, 24V1, 0V1, 24V2, 0V2 | Continuity present between respective TBs | Multimeter | No | 8 |  |  |  | Manual
HW-004 | Hardware Config | 4.1 Pre-check | Earthing connections continuity | All earth points continuous | Multimeter | No | 8 |  |  |  | Manual
HW-005 | Hardware Config | 4.1 Pre-check | SMPS1 & SMPS2 output supply wiring continuity | Continuous | Multimeter | No | 8 |  |  |  | Manual
HW-006 | Hardware Config | 4.1 Pre-check | AC meter V1/V2/V3/N to MCCB L1/L2/L3/N continuity | Continuous, correct phase mapping | Multimeter | No | 8 |  |  |  | Manual
HW-007 | Hardware Config | 4.1 Pre-check | No short between 24V1 & 24V2 | No continuity (open) | Multimeter | No | 8 | Critical - must be isolated |  |  | Manual
HW-008 | Hardware Config | 4.1 Pre-check | Fuses open + supply removed for AB, HMI, SECC J1, CPPP J6 | De-energised before power-up | Procedure step | No | 8 |  |  |  | Manual
HW-009 | Hardware Config | 4.1 Pre-check | 3-phase supply to MCCB verified then MCCB ON | Correct 3ph voltage present | Multimeter | No | 8 |  |  |  | Manual
HW-010 | Hardware Config | 4.1 Pre-check | SMPS1 & 2 AC input / DC output then close fuses | Correct AC in / DC out | Multimeter | No | 8 |  |  |  | Manual
HW-011 | Hardware Config | 4.1 Pre-check | DC jack cable for AB voltage | 5 V | Multimeter | No | 8 |  |  |  | Manual
HW-012 | Hardware Config | 4.1 Pre-check | DC jack cable for HMI voltage | 24 V | Multimeter | No | 8 |  |  |  | Manual
HW-013 | Hardware Config | 4.1 Pre-check | SECC_J1 voltage | 24 V | Multimeter | No | 8 |  |  |  | Manual
HW-014 | Hardware Config | 4.1 Pre-check | CPPP_J8 voltage | 24 V | Multimeter | No | 8 |  |  |  | Manual
HW-015 | Hardware Config | 4.1 Pre-check | SECC-LE_J1 voltage | 24 V | Multimeter | No | 8 |  |  |  | Manual
HW-016 | Hardware Config | 4.1 Pre-check | DC meter supply voltage | 24 V | Multimeter | No | 8 |  |  |  | Manual
HW-017 | Hardware Config | 4.1 Pre-check | All components power on after supply restored | Boards/HMI power up | Visual | No | 8 |  |  |  | Manual
HW-018 | Hardware Config | 4.1 Pre-check | Touch screen functionality | Touch responsive | Visual / manual | No | 8 |  |  |  | Manual
HW-019 | Hardware Config | 4.2 PM address | Power Module 1 address | Binary 0 (default) | DIP switch | No | 8 | 6 x 30kW modules |  |  | Manual
HW-020 | Hardware Config | 4.2 PM address | Power Module 2 address | Binary 1 | DIP switch | No | 8 |  |  |  | Manual
HW-021 | Hardware Config | 4.2 PM address | Power Module 3 address | Binary 2 | DIP switch | No | 8 |  |  |  | Manual
HW-022 | Hardware Config | 4.2 PM address | Power Module 4 address | Binary 3 | DIP switch | No | 8 |  |  |  | Manual
HW-023 | Hardware Config | 4.2 PM address | Power Module 5 address | Binary 4 | DIP switch | No | 9 |  |  |  | Manual
HW-024 | Hardware Config | 4.2 PM address | Power Module 6 address | Binary 5 | DIP switch | No | 9 |  |  |  | Manual
HW-025 | Hardware Config | 4.2 ELR | ELR leakage current setpoint | 0.1 In (A) | Rotary dial | No | 9 | GIC ELR |  |  | Manual
HW-026 | Hardware Config | 4.2 ELR | ELR trip time setpoint | 1 dt (S) | Rotary dial | No | 9 |  |  |  | Manual
HW-027 | Hardware Config | 4.2 IMD | Both IMDs same address; DIP 4-8 enabled | DIP 4..8 ON on both IMD (10-switch) | DIP switch | No | 12 | Q10_IMD1/2 |  |  | Manual
HW-028 | Hardware Config | 4.2 AC meter | Primary CT current rating | 200 A | Meter keypad (CT Primary) | Partial | 13 | Set on meter; verify via IO Mapper readback |  |  | Hybrid
HW-029 | Hardware Config | 4.2 AC meter | Network selection | 3P4W | Meter keypad | No | 13 | Factory default 3P4W |  |  | Manual
HW-030 | Hardware Config | 4.2 AC meter | Phase sequence check | Display reads 'OK - CLK' | Hold 'V' 3s | No | 15 |  |  |  | Manual
HW-031 | Hardware Config | 4.2 AC meter | Current connection indication | Display reads '23' (L2&L3 reversed = required) | Hold 'I' 3s | No | 15 | If 0: swap S1/S2 on L2&L3 CT; if 13: swap L1&L2; reboot, re-check =23 |  |  | Manual
HW-032 | Hardware Config | 4.2 DC meter | Modbus address | Add-002 | DC meter keypad (pwd 1101) | Partial | 17 | Verify via IO Mapper |  |  | Hybrid
HW-033 | Hardware Config | 4.2 DC meter | Parity | None | DC meter keypad | Partial | 17 |  |  |  | Hybrid
HW-034 | Hardware Config | 4.2 DC meter | Shunt current rating CH1 / CH2 | SH1 = 500 A, SH2 = 500 A | DC meter keypad | Partial | 17 |  |  |  | Hybrid
SW-001 | Software Config | 4.2 Router | Router model / make | RB44 / Silbo | Inspect / web UI | No | 9 |  |  |  | Manual
SW-002 | Software Config | 4.2 Router | Connect to router SSID (AP_*) & login | Pwd 12345678; UI 192.168.1.1; admin/admin | Web UI | No | 9 | Initial setup only |  |  | Manual
SW-003 | Software Config | 4.2 Router | Router LAN/Ethernet static IP | 10.20.27.1 (saved & updated) | Web UI > Network > Ethernet | Partial | 10 | Verify by reaching 10.20.27.1 |  |  | Hybrid
SW-004 | Software Config | 4.2 Router | Router reachable on new IP after update | 10.20.27.1 loads; admin/admin | HTTP GET | Yes | 11 |  |  |  | Automated
SW-005 | Software Config | 4.2 Router | WIFI client SSID + passphrase set; internet up | Router connected to internet (WAN up) | Web UI > WIFI Settings | Partial | 11-12 | Client SSID/pass site-specific |  |  | Hybrid
SW-006 | Software Config | 4.2 SECC update | SECC firmware updated to latest release | Update 100% + reboot; firmware = target release | LWI 10.20.27.100 > Update View | Partial | 17-18 | Upload .ecog-update; verify version readback |  |  | Hybrid
SW-007 | Software Config | 4.2 SECC-LE update | SECC-LE firmware updated to latest release | Update 100% + reboot; firmware = target release | LWI 10.20.27.101 > Update View | Partial | 18 | Select SECC-LE update file |  |  | Hybrid
SW-008 | Software Config | 4.2 SECC/LE config | num_of_module | 6 | LWI > Advance > Configuration | Yes | 19 | Set on BOTH SECC & SECC-LE then Load to device |  |  | Hybrid
SW-009 | Software Config | 4.2 SECC/LE config | maxKW | 180 | LWI > Advance > Configuration | Yes | 19 |  |  |  | Hybrid
SW-010 | Software Config | 4.2 SECC/LE config | maxA | 500 | LWI > Advance > Configuration | Yes | 19 |  |  |  | Hybrid
SW-011 | Software Config | 4.2 SECC/LE config | dlbMode | quintupleCombo | LWI > Advance > Configuration | Yes | 19 | 180kW ADLB DLB mode |  |  | Hybrid
SW-012 | Software Config | 4.2 AB update | AB firmware updated to latest release | 'installation successful' + reboot; firmware = target release | Swagger 10.20.27.50:3001 / ab-update-win.exe | Partial | 19-20 | GET /release to verify |  |  | Hybrid
SW-013 | Software Config | 4.2 AB config | chargingPointModel | Customer Name (Mahindra) | POST /ocpp-client/config | Yes | 20-21 | GET /ocpp-client/config to verify |  |  | Automated
SW-014 | Software Config | 4.2 AB config | chargePointSerialNumber | Per unit serial no. | POST /ocpp-client/config | Yes | 20-21 | Unit-specific |  |  | Automated
SW-015 | Software Config | 4.2 AB config | powerSaveInIdleMode | true/false per requirement | POST /ocpp-client/config | Yes | 20-21 | Customer-dependent; confirm intent |  |  | Automated
SW-016 | Software Config | 4.2 AB config | chargingPointVendor | QUENCH | GET /ocpp-client/config | Yes | 21 |  |  |  | Automated
SW-017 | Software Config | 4.2 AB config | protocol | ocpp1.6 | GET /ocpp-client/config | Yes | 21 |  |  |  | Automated
SW-018 | Software Config | 4.2 AB config | OCPPEndpointToBackend | Valid CMS WebSocket URL | GET /ocpp-client/config | Yes | 21 | Customer CMS endpoint |  |  | Automated
SW-019 | Software Config | 4.2 AB config | RFIDEnabled | true | GET /ocpp-client/config | Yes | 21 |  |  |  | Automated
SW-020 | Software Config | 4.2 AB config | maxPowerLimitInkW (AB OCPP key) | VERIFY for 180kW (example shows 80) | GET /ocpp-client/config | Yes | 21 | DISCREPANCY: example=80 is a 60kW ref. Confirm intended value vs SECC maxKW=180; do not auto-correct if intentional CMS cap |  |  | Automated
SW-021 | Software Config | 4.2 AB config | maxCurrentLimitInAmps (AB OCPP key) | VERIFY for 180kW (example shows 200) | GET /ocpp-client/config | Yes | 21 | DISCREPANCY: example=200 vs SECC maxA=500. Confirm intended value |  |  | Automated
SW-022 | Software Config | 4.2 AB config | NumberOfConnectors | 2 | GET /ocpp-client/config | Yes | 22 | Dual-gun CCS2 |  |  | Automated
SW-023 | Software Config | 4.2 AB config | HeartbeatInterval | 300 (standard block) | GET /ocpp-client/config | Yes | 22 | Note: separate HeartBeatInterval=30 also present - verify intended |  |  | Automated
SW-024 | Software Config | 4.2 AB config | MeterValuesSampledData populated | Includes Energy.Active.Import.Register, SoC, Current/Voltage etc. | GET /ocpp-client/config | Yes | 22 |  |  |  | Automated
SW-025 | Software Config | 4.2 AB config | dataTransfer VendorsId / MessagesId | VendorsId=[MSIL], MessagesId=[AutoStop] | GET /ocpp-client/config | Yes | 23 | MSIL = Maruti? confirm vs Mahindra build |  |  | Automated
SW-026 | Software Config | 4.3 Comm test | Power module CAN communication | All 6 modules communicating | SECC LWI > IO Mapper | Yes | 24 |  |  |  | Automated
SW-027 | Software Config | 4.3 Comm test | Selec AC meter online | modbus.selec.online = true | IO Mapper | Yes | 24 |  |  |  | Automated
SW-028 | Software Config | 4.3 Comm test | AC meter 3-phase V & I present, matches display | Live V/I/PF; actual == display | IO Mapper | Yes | 24 | voltage_L1~243, L-L~420 |  |  | Automated
SW-029 | Software Config | 4.3 Comm test | Dfun DC meter online | modbus.dfun_dc.online = true | IO Mapper | Yes | 25 |  |  |  | Automated
SW-030 | Software Config | 4.3 Comm test | DC meter CH1 & CH2 params present | CH1/CH2 Energy, Power, Voltage, Current readable | IO Mapper | Yes | 25 |  |  |  | Automated
SW-031 | Software Config | 4.3 Comm test | Gongyuan IMD online | modbus.gongyuan_IMD.online = true | IO Mapper | Yes | 25 |  |  |  | Automated
SW-032 | Software Config | 4.3 Comm test | IMD insulation resistance (during cable check/charging) | 60000 (>= 10 Mohm). 65535 => <= 10 Mohm (fault) | IO Mapper | Partial | 25 | Idle dump may read 65535 when not measuring; assert 60000 only during cable check/charge |  |  | Hybrid
SW-033 | Software Config | 4.3 Comm test (idle) | AC meter sign convention - idle | Avg PF +; Active L1 +, L2 -, L3 - | IO Mapper | Yes | 16 | Confirms CT direction correct |  |  | Automated
SW-034 | Software Config | 4.3 Comm test (charging) | AC meter sign convention - charging | Avg PF + ~0.9; Active L1/L2/L3 all +; only active_import_total increasing; export = 0 | IO Mapper | Partial | 16 | Needs active charge session |  |  | Hybrid
SW-035 | Software Config | 4.4 Charging A | Verify AC & DC contactors + control relays | Switch correctly per Maintenance Mode Manual | Maint. mode / LWI | Partial | 26 |  |  |  | Hybrid
SW-036 | Software Config | 4.4 Charging A | Gun A pilot state on EV connect | B connected, HiCom active | LWI 10.20.27.100 | Yes | 26 |  |  |  | Hybrid
SW-037 | Software Config | 4.4 Charging A | Authorize & start charge (Gun A) | Session starts on Auth | LWI / CMS | Partial | 26 |  |  |  | Hybrid
SW-038 | Software Config | 4.4 Charging A | Battery SOC matches vehicle display | SOC equal to vehicle | HMI vs vehicle | Partial | 26 |  |  |  | Hybrid
SW-039 | Software Config | 4.4 Charging A | EV demand current == supply current | Demand A == supply A | LWI / HMI | Yes | 26 |  |  |  | Hybrid
SW-040 | Software Config | 4.4 Charging A | Display functionality during session | Live V/I/Power/SOC/temps shown | HMI | Partial | 26 |  |  |  | Manual
SW-041 | Software Config | 4.4 Charging A | Start sequence: cable check + pre-charge | Both stages complete OK | LWI | Yes | 26 |  |  |  | Hybrid
SW-042 | Software Config | 4.4 Charging A | Stop sequence: finishing | Clean stop / finishing state | LWI / HMI | Yes | 26 |  |  |  | Hybrid
SW-043 | Software Config | 4.4 Charging B | Repeat full charging session on Gun B | Same pass criteria as Gun A | LWI 10.20.27.101 | Partial | 27 |  |  |  | Hybrid
SW-044 | Software Config | 4.5 OCPP | Connect to CMS (config + start + restart) | POST config (WS URL+ID), POST start, POST restart all 200 | Swagger 10.20.27.50:3001 | Yes | 27-28 |  |  |  | Automated
SW-045 | Software Config | 4.5 OCPP | Cloud sign on HMI | Cloud/connected icon shown | HMI | Partial | 29 | Indicates CMS connected |  |  | Automated
SW-046 | Software Config | 4.5 OCPP | Authorization methods work | OTP, RFID, Remote all authorize | CMS / HMI | Partial | 29 |  |  |  | Hybrid
SW-047 | Software Config | 4.5 OCPP | Idle-state error codes | Codes per Error Codes List; CMS log, screen, HMI alarm log consistent | CMS log / HMI | Partial | 29 |  |  |  | Hybrid
SW-048 | Software Config | 4.5 OCPP | Manual/Maintenance mode DC contactor test | Manual contactor switching verified | Maintenance Mode Manual | No | 29 |  |  |  | Manual
SW-049 | Software Config | 4.5 OCPP | Full charging session per OCPP test doc | Session completes per OCPP doc | CMS | Partial | 29 |  |  |  | Hybrid
SW-050 | Software Config | 4.5 OCPP | Offline OTP + 2 RFID in local auth list | localAuthorizationList has OTP idTag + 2 RFID, status Accepted, updateType Full | Swagger POST localAuthList / GET config | Yes | 29-30 | Verify via GET after upload |  |  | Hybrid
SW-051 | Software Config | 4.5 OCPP | Reset AC meter energy after OCPP test | AC meter energy reset to 0 | AC meter manual (p13) | No | 31 |  |  |  | Manual
SW-052 | Software Config | 4.5 OCPP | Reset DC meter energy after OCPP test | DC meter energy zeroed via 'Zero Clear' | Dfun debug SW (RS485-USB, COM/9600/EVEN) | No | 31-33 | admin/admin; Meter Clear > Zero Clear |  |  | Manual

## Summary
Category | Total | Automated | Hybrid | Manual
Physical | 23 | 0 | 0 | 23
Hardware Config | 34 | 0 | 4 | 30
Software Config | 52 | 23 | 23 | 6
TOTAL | 109 | 23 | 27 | 59